## Sheet1
#VALUE!
Make Up Air/Duct Furnace Start Up Sheet |  |  |  |  | Date:
Checked? | Description | Recording | Recording | Recording | Recording | Notes
Inspect the unit for damage
Inspect installation
Incoming power wires should be terminated and secure
Check all factory connections, terminated wires should be secure
Shipped loose items wired and terminated in the unit at their proper terminal blocks
Incoming gas line terminated at the unit, gas line has been purged
Check all factory wiring
Check set screws and all moving components
Check inlet gas pressure to the unit, should not exceed 14” W.C.
Check incoming voltage to the unit, should match the unit data tag
Control voltage should be 24 volts or greater, normal voltage around 27 volts
Check, record supply fan data tag information
Check overload setting on motor starter (if applicable) confirm that setting are set at approximately 1.5% higher that supply fan FLA
Activate supply fan, check for correct rotation
Check amp draw on the supply fan, if amperage is too high, adjust motor pulley
Activate the heating circuit at high fire
Check inlet gas pressure with unit at high fire, inlet pressure should be greater than the minimum inlet pressure reading on the data tag (normally 5” W.C.)
Check manifold pressure, high fire, should be at 3.5” W.C. for natural gas, two stage operation should be at 1.8” W.C. at low fire.
Check operation of field installed devices